## Slide 1: 2f. Feeder 04 Reduced OpenDSS Model

## Slide 2: Capture of DSDR Operations on Feeder 04
The primary function of DSDR is to perform demand reduction at peak loading conditions by dropping OLTC and feeder SVR voltage set points system wide.
A 1% change in voltage results in a 0.2% to 1.5% change in real power and a 2% to 6% change in reactive power.
SC operations pulled from DSCADA historian. SC states stacked on top of one another with higher number out of pair signifying the “on” state.
(a) Derived Annual Q
(b) Historical S.C. States

## Slide 3: One Week QSTS Sim. Between DOY 164 to 171
It was concluded the DSDR program enforces a priority system in which the order goes SC1, SC2, and then SC3.
For example, if reactive power level was observed greater than threshold and only SC1 is energized, a command would be sent to SC2 to trip on-line for PF correction, therefore flattening the voltage profile and decreasing losses.
(a) Locations of V.R. Equipment
(b) States of S.C. Banks

## Slide 4: 5a. Variable Nature of Solar Gen.

## Slide 5: Simplifying the Feeder 04 Model
Topology Planning
Topology Results

## Slide 6: Simplifying the Feeder 04 Model
Component Comparison
 | Detailed | Simplified | Reduction
Lines | 2196 | 67 | 96.9%
Loads | 1047 | 78 | 92.6%
DSS Line/Bus Development
Example DSS Line/Bus Development
New Line.K1 Phases=3 Bus1=08_1.1.2.3 Bus2=08_A1.1.2.3
~ Length=2833.6 units=ft Spacing=PEC_PEC_23kV_TRIA_3P
~ wires=['PEC_#2AWG_ACSR' 'PEC_#2AWG_ACSR' 'PEC_#2AWG_ACSR' 'PEC_#2AWG_ACSR']

## Slide 7: Static Power Flow
Detailed
Simplified

## Slide 8: Static Power Flow
Detailed
Simplified

## Slide 9: 24 Hour QSTS kW
SCADA
Model

## Slide 10: 24 Hour QSTS kVAR
SCADA
Model

## Slide 11: 1 Week QSTS
kW vs. Time
Voltage vs. Time

## Slide 12: Benefits & Future Work
After model completion, we will begin to compare the runtime of the simplified and detailed model
We will use the simplified model to investigate MATLAB control of SVRs